## component
id | name | nistir_subelement
B2011.A | CFS Exterior Walls | B2011
B2011.B | Light-framed Wood Exterior Walls | B2011
D2022.A | Domestic Water Piping - Horizontal Mains and Branches | D2022

## experiment
id | reference | specimen | specimen_inspection_sequence | reviewer | component | comp_detail | material | size_class | test_type | loading_protocol | peak_test_amplitude | location | governing_design_standard | design_objective | comp_description | ds_description | prior_damage | prior_damage_repaired | edp_metric | edp_unit | edp_value | alt_edp_metric | alt_edp_unit | alt_edp_value | ds_rank | ds_class | notes
exp1502a | ARA-2012-EXP | 81.0 |  | NIST | D2022.A | Hospital distrubution system - Braced | Steel |  | Dynamic, uniaxial | Synthetic table input motion compatible with AC156 response spectrum | Peak acceleration = 1.31g Peak displacement= 8.65 in (4.3% inter-story drift) Increasing Intensities of IM from 5% to 100% of full scale motion | NEES, University of Nevada, Reno |  |  | RESTRAINED and WELDED Assembly Two water heaters (attached to shake table), one heat exchanger (atatched to shake table), three riser branches, and horizontal runs. The piping assembly consists of 3in (out dia=3.5 in, thickness=0.216 in) and 4 in (out dia=4.5 in, thickness=0.237 in) schedule 40 ASTM A53 Grade B black steel pipe. Water heater connected to 3 in file through four-bolt flanged connectionHeat Exhanger and all valves connected to 4 in pipe through eght-bolt flanged connectionHydrostatic pressure1/8 in dia galvanized 7 no.s of strands x19 wires per strand aircraft grade steel (with min break strength of 1700lbs) Cable restrainers used as seismic bracing 5/8 in dia all threaded rods for 4-in pipes /2 in dia all threaded rods for 3-in pipes Vertical hanger rods braced laterally along their length with a 1 5/8 in sq, 12 gauge strut to prevent buckling cross bolts in hanger clevises Welded assemblies (Root material E6010 and fill material E7018). Each joint was prepared with a 65o, 3/32-in root and 3/32-in landing. | Flanged connection joining the heat exchanger to the pipe began to leak (100% IM) |  |  | Story Drift Ratio | Ratio | 0.043 |  |  |  |  | Consequential
exp1502a | ARA-2012-EXP | 81.0 |  | NIST | D2022.A | Hospital distrubution system - Braced | Steel |  | Dynamic, uniaxial | Synthetic table input motion compatible with AC156 response spectrum | Peak acceleration = 1.31g Peak displacement= 8.65 in (4.3% inter-story drift) Increasing Intensities of IM from 5% to 100% of full scale motion | NEES, University of Nevada, Reno |  |  | RESTRAINED and WELDED Assembly Two water heaters (attached to shake table), one heat exchanger (atatched to shake table), three riser branches, and horizontal runs. The piping assembly consists of 3in (out dia=3.5 in, thickness=0.216 in) and 4 in (out dia=4.5 in, thickness=0.237 in) schedule 40 ASTM A53 Grade B black steel pipe. Water heater connected to 3 in file through four-bolt flanged connectionHeat Exhanger and all valves connected to 4 in pipe through eght-bolt flanged connectionHydrostatic pressure1/8 in dia galvanized 7 no.s of strands x19 wires per strand aircraft grade steel (with min break strength of 1700lbs) Cable restrainers used as seismic bracing 5/8 in dia all threaded rods for 4-in pipes /2 in dia all threaded rods for 3-in pipes Vertical hanger rods braced laterally along their length with a 1 5/8 in sq, 12 gauge strut to prevent buckling cross bolts in hanger clevises Welded assemblies (Root material E6010 and fill material E7018). Each joint was prepared with a 65o, 3/32-in root and 3/32-in landing. | Flanged connection joining the heat exchanger to the pipe began to leak (100% IM) |  |  | Story Drift Ratio | Ratio | 0.043 |  |  |  |  | Consequential

## experiment_fragility_bridge
experiment | fragility_model
exp1502a | B2011.001a

## fragility_curve
fragility_model | reviewer | source | basis | num_observations | reference | edp_metric | edp_unit | ds_rank | ds_description | median | beta | probability
B2011.001a | NIST | Literature | Experiment |  | ARA-2012-EXP | Joint Rotation | Radians | 1 | First Leakage | 0.006 | 0.204

## fragility_model
id | p58_fragility | component | comp_detail | material | size_class | comp_description
B2011.001a | B2011.001a | B2011.A |  |  |  | Exterior Wall - Cold formed steel walls with wood structural panel sheathing, interior - gypsum board - Costing for each 100 ft^2 Wall Panel. Assumed framing: 38 mil cold formed steel framing with 7/16 OSB and 3/8 plywood panel sheathing with overturning restraint at each end of the wall per AISI design standard. No. 8 screws 2" to 6" OC at perimeter and 12" OC EW in field.
B2011.001b | B2011.001b | B2011.A |  |  |  | Exterior Wall - Cold formed steel walls with wood structural panel sheathing, exterior - stucco one side - Costing for each 100 ft^2 Wall Panel. Assumed framing: 38 mil cold formed steel framing with 7/16 OSB and 3/8 plywood panel sheathing with overturning restraint at each end of the wall per AISI design standard. No. 8 screws 2" to 6" OC at perimeter and 12" OC EW in field.

## reference
id | study_type | comp_type | csl_data.type | csl_data.id | csl_data.title | csl_data.author | csl_data.issued.date-parts | csl_data.DOI | csl_data.URL | csl_data.event-title | csl_data.event-place | csl_data.note
ARA-2012-EXP | Experiment | Hospital Piping Assembly | document | ARA-2012-EXP | Experimental and Analytical Studies of Hospital Piping Assemblies Subjected to Seismic Loading | [{'family': 'Zaghi', 'given': 'Arash E.'}, {'family': 'Maragakis', 'given': 'E.'}, {'family': 'Itani', 'given': 'Ahmad'}, {'family': 'Goodwin', 'given': 'Elliot'}] | [[2012]] | https://doi.org/10.1193/1.3672911 | https://doi.org/10.1193/1.3672911
ARA-2012-NOV | Experiment | Partition Walls | paper-conference | ARA-2012-NOV | Novel Sliding/frictional Connections for Improved Seismic Performance of Gypsum Wallboard Partitions | [{'family': 'Araya-Letelier'}, {'family': 'Miranda'}] | [[2012]] | https://doi.org/10.1193/1.3672911 | https://doi.org/10.1193/1.3672911 | 15th World Conference on Earthquake Engineering | Lisbon, Portugal | Araya-Letelier, Gerardo and Miranda, Eduardo. (2012). Novel Sliding/Frictional Connections for Improved Seismic Performance of Gypsum Wallboard Partitions. 15th World Conference on Earthquake Engineering, Lisbon, Portugal.